## Signals
Intesis MAPS Excel signals file
PROJECT_NAME | MH-AC-MBS.ibmaps
Intesis MAPS Version | 1.2.31.0
Internal Protocol | Modbus Slave
External Protocol | Mitsubishi Heavy Industries
Timestamp | 07/27/2026
# | Active | Description | Data Length | Format | Address | Bit | Read / Write | String Length | # | Unit ID | IU | OU
1 | True | Gateway Communication Status (0-No Error, 1-Failure) | 16 | 0: Unsigned | 2995 | - | 0: Read | - | 1 | - | - | -
2 | True | On/Off (all the units) (0-Off, 1-On) | 16 | 0: Unsigned | 2996 | - | 2: Read / Write | - | 2 | - | - | -
3 | True | Operation Mode (all the units) (0-Cool, 1-Heat, 2-Fan, 3-Auto, 4-Dry) | 16 | 0: Unsigned | 2997 | - | 2: Read / Write | - | 3 | - | - | -
4 | True | Setpoint (all the units) (16..30ºC) (x10) | 16 | 1: Signed (C2) | 2998 | - | 2: Read / Write | - | 4 | - | - | -
5 | True | Fan Speed (all the units) (0-Low, 1-Medium, 2-High, 3-Powerful) | 16 | 0: Unsigned | 2999 | - | 2: Read / Write | - | 5 | - | - | -
6 | True | Remote Lock (all the units) (1-Lock, 0-Unlock) | 16 | 0: Unsigned | 3000 | - | 2: Read / Write | - | 6 | - | - | -
7 | True | Communication Status (0-No Error, 1-Error) | 16 | 0: Unsigned | 1 | - | 0: Read | - | 7 | Unit 1 - 101 | 1 | -
8 | True | On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 2 | - | 2: Read / Write | - | 8 | Unit 1 - 101 | 1 | -
9 | True | Operation Mode (0-Cool, 1-Heat, 2-Fan, 3-Auto, 4-Dry) | 16 | 0: Unsigned | 3 | - | 2: Read / Write | - | 9 | Unit 1 - 101 | 1 | -
10 | True | Temperature Setpoint (16..30ºC) (x10) | 16 | 1: Signed (C2) | 4 | - | 2: Read / Write | - | 10 | Unit 1 - 101 | 1 | -
11 | True | Fan Speed (0-Low, 1-Medium, 2-High, 3-Powerful) | 16 | 0: Unsigned | 5 | - | 2: Read / Write | - | 11 | Unit 1 - 101 | 1 | -
12 | True | Remote Lock (0-Unlock, 1-Lock) | 16 | 0: Unsigned | 6 | - | 2: Read / Write | - | 12 | Unit 1 - 101 | 1 | -
13 | True | Louver / Vane Position (0-Swing, 1-Pos1, 2-Pos2, 3-Pos3, 4-Pos4) | 16 | 0: Unsigned | 7 | - | 2: Read / Write | - | 13 | Unit 1 - 101 | 1 | -
14 | True | Room Temperature (16..30ºC) (x10) | 16 | 0: Unsigned | 8 | - | 0: Read | - | 14 | Unit 1 - 101 | 1 | -
15 | True | Filter Sign Status (0-Off, 1-On) | 16 | 0: Unsigned | 9 | - | 0: Read | - | 15 | Unit 1 - 101 | 1 | -
16 | True | Unit Error code (0-No Error,X-Error(1..255)) | 16 | 0: Unsigned | 10 | - | 0: Read | - | 16 | Unit 1 - 101 | 1 | -
17 | True | Compressor Status (0-Off, 1-On) | 16 | 0: Unsigned | 11 | - | 0: Read | - | 17 | Unit 1 - 101 | 1 | -
18 | True | Filter Sign Reset (1-Reset) | 16 | 0: Unsigned | 12 | - | 1: Trigger | - | 18 | Unit 1 - 101 | 1 | -
19 | True | RC Error Reset (1-Reset) | 16 | 0: Unsigned | 13 | - | 1: Trigger | - | 19 | Unit 1 - 101 | 1 | -
20 | True | Thermo On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 14 | - | 0: Read | - | 20 | Unit 1 - 101 | 1 | -
21 | True | Expansion valve opening pulse status (000..999) | 16 | 0: Unsigned | 15 | - | 0: Read | - | 21 | Unit 1 - 101 | 1 | -
22 | False | Decision frequency status (0..255Hz) | 16 | 0: Unsigned | 16 | - | 0: Read | - | 22 | Unit 1 - 101 | 1 | -
23 | False | Demand frequency status (0..255Hz) | 16 | 0: Unsigned | 17 | - | 0: Read | - | 23 | Unit 1 - 101 | 1 | -
24 | False | Heat Exchange low 1 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 18 | - | 0: Read | - | 24 | Unit 1 - 101 | 1 | -
25 | False | Heat Exchange low 2 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 19 | - | 0: Read | - | 25 | Unit 1 - 101 | 1 | -
26 | False | Heat Exchange low 3 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 20 | - | 0: Read | - | 26 | Unit 1 - 101 | 1 | -
27 | True | Communication Status (0-No Error, 1-Error) | 16 | 0: Unsigned | 21 | - | 0: Read | - | 27 | Unit 2 - 102 | 2 | -
28 | True | On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 22 | - | 2: Read / Write | - | 28 | Unit 2 - 102 | 2 | -
29 | True | Operation Mode (0-Cool, 1-Heat, 2-Fan, 3-Auto, 4-Dry) | 16 | 0: Unsigned | 23 | - | 2: Read / Write | - | 29 | Unit 2 - 102 | 2 | -
30 | True | Temperature Setpoint (16..30ºC) (x10) | 16 | 1: Signed (C2) | 24 | - | 2: Read / Write | - | 30 | Unit 2 - 102 | 2 | -
31 | True | Fan Speed (0-Low, 1-Medium, 2-High, 3-Powerful) | 16 | 0: Unsigned | 25 | - | 2: Read / Write | - | 31 | Unit 2 - 102 | 2 | -
32 | True | Remote Lock (0-Unlock, 1-Lock) | 16 | 0: Unsigned | 26 | - | 2: Read / Write | - | 32 | Unit 2 - 102 | 2 | -
33 | True | Louver / Vane Position (0-Swing, 1-Pos1, 2-Pos2, 3-Pos3, 4-Pos4) | 16 | 0: Unsigned | 27 | - | 2: Read / Write | - | 33 | Unit 2 - 102 | 2 | -
34 | True | Room Temperature (16..30ºC) (x10) | 16 | 0: Unsigned | 28 | - | 0: Read | - | 34 | Unit 2 - 102 | 2 | -
35 | True | Filter Sign Status (0-Off, 1-On) | 16 | 0: Unsigned | 29 | - | 0: Read | - | 35 | Unit 2 - 102 | 2 | -
36 | True | Unit Error code (0-No Error,X-Error(1..255)) | 16 | 0: Unsigned | 30 | - | 0: Read | - | 36 | Unit 2 - 102 | 2 | -
37 | True | Compressor Status (0-Off, 1-On) | 16 | 0: Unsigned | 31 | - | 0: Read | - | 37 | Unit 2 - 102 | 2 | -
38 | True | Filter Sign Reset (1-Reset) | 16 | 0: Unsigned | 32 | - | 1: Trigger | - | 38 | Unit 2 - 102 | 2 | -
39 | True | RC Error Reset (1-Reset) | 16 | 0: Unsigned | 33 | - | 1: Trigger | - | 39 | Unit 2 - 102 | 2 | -
40 | True | Thermo On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 34 | - | 0: Read | - | 40 | Unit 2 - 102 | 2 | -
41 | True | Expansion valve opening pulse status (000..999) | 16 | 0: Unsigned | 35 | - | 0: Read | - | 41 | Unit 2 - 102 | 2 | -
42 | False | Decision frequency status (0..255Hz) | 16 | 0: Unsigned | 36 | - | 0: Read | - | 42 | Unit 2 - 102 | 2 | -
43 | False | Demand frequency status (0..255Hz) | 16 | 0: Unsigned | 37 | - | 0: Read | - | 43 | Unit 2 - 102 | 2 | -
44 | False | Heat Exchange low 1 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 38 | - | 0: Read | - | 44 | Unit 2 - 102 | 2 | -
45 | False | Heat Exchange low 2 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 39 | - | 0: Read | - | 45 | Unit 2 - 102 | 2 | -
46 | False | Heat Exchange low 3 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 40 | - | 0: Read | - | 46 | Unit 2 - 102 | 2 | -
47 | True | Communication Status (0-No Error, 1-Error) | 16 | 0: Unsigned | 41 | - | 0: Read | - | 47 | Unit 3 - 104 | 4 | -
48 | True | On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 42 | - | 2: Read / Write | - | 48 | Unit 3 - 104 | 4 | -
49 | True | Operation Mode (0-Cool, 1-Heat, 2-Fan, 3-Auto, 4-Dry) | 16 | 0: Unsigned | 43 | - | 2: Read / Write | - | 49 | Unit 3 - 104 | 4 | -
50 | True | Temperature Setpoint (16..30ºC) (x10) | 16 | 1: Signed (C2) | 44 | - | 2: Read / Write | - | 50 | Unit 3 - 104 | 4 | -
51 | True | Fan Speed (0-Low, 1-Medium, 2-High, 3-Powerful) | 16 | 0: Unsigned | 45 | - | 2: Read / Write | - | 51 | Unit 3 - 104 | 4 | -
52 | True | Remote Lock (0-Unlock, 1-Lock) | 16 | 0: Unsigned | 46 | - | 2: Read / Write | - | 52 | Unit 3 - 104 | 4 | -
53 | True | Louver / Vane Position (0-Swing, 1-Pos1, 2-Pos2, 3-Pos3, 4-Pos4) | 16 | 0: Unsigned | 47 | - | 2: Read / Write | - | 53 | Unit 3 - 104 | 4 | -
54 | True | Room Temperature (16..30ºC) (x10) | 16 | 0: Unsigned | 48 | - | 0: Read | - | 54 | Unit 3 - 104 | 4 | -
55 | True | Filter Sign Status (0-Off, 1-On) | 16 | 0: Unsigned | 49 | - | 0: Read | - | 55 | Unit 3 - 104 | 4 | -
56 | True | Unit Error code (0-No Error,X-Error(1..255)) | 16 | 0: Unsigned | 50 | - | 0: Read | - | 56 | Unit 3 - 104 | 4 | -
57 | True | Compressor Status (0-Off, 1-On) | 16 | 0: Unsigned | 51 | - | 0: Read | - | 57 | Unit 3 - 104 | 4 | -
58 | True | Filter Sign Reset (1-Reset) | 16 | 0: Unsigned | 52 | - | 1: Trigger | - | 58 | Unit 3 - 104 | 4 | -
59 | True | RC Error Reset (1-Reset) | 16 | 0: Unsigned | 53 | - | 1: Trigger | - | 59 | Unit 3 - 104 | 4 | -
60 | True | Thermo On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 54 | - | 0: Read | - | 60 | Unit 3 - 104 | 4 | -
61 | True | Expansion valve opening pulse status (000..999) | 16 | 0: Unsigned | 55 | - | 0: Read | - | 61 | Unit 3 - 104 | 4 | -
62 | False | Decision frequency status (0..255Hz) | 16 | 0: Unsigned | 56 | - | 0: Read | - | 62 | Unit 3 - 104 | 4 | -
63 | False | Demand frequency status (0..255Hz) | 16 | 0: Unsigned | 57 | - | 0: Read | - | 63 | Unit 3 - 104 | 4 | -
64 | False | Heat Exchange low 1 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 58 | - | 0: Read | - | 64 | Unit 3 - 104 | 4 | -
65 | False | Heat Exchange low 2 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 59 | - | 0: Read | - | 65 | Unit 3 - 104 | 4 | -
66 | False | Heat Exchange low 3 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 60 | - | 0: Read | - | 66 | Unit 3 - 104 | 4 | -
67 | True | Communication Status (0-No Error, 1-Error) | 16 | 0: Unsigned | 61 | - | 0: Read | - | 67 | Unit 4 - 106 | 6 | -
68 | True | On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 62 | - | 2: Read / Write | - | 68 | Unit 4 - 106 | 6 | -
69 | True | Operation Mode (0-Cool, 1-Heat, 2-Fan, 3-Auto, 4-Dry) | 16 | 0: Unsigned | 63 | - | 2: Read / Write | - | 69 | Unit 4 - 106 | 6 | -
70 | True | Temperature Setpoint (16..30ºC) (x10) | 16 | 1: Signed (C2) | 64 | - | 2: Read / Write | - | 70 | Unit 4 - 106 | 6 | -
71 | True | Fan Speed (0-Low, 1-Medium, 2-High, 3-Powerful) | 16 | 0: Unsigned | 65 | - | 2: Read / Write | - | 71 | Unit 4 - 106 | 6 | -
72 | True | Remote Lock (0-Unlock, 1-Lock) | 16 | 0: Unsigned | 66 | - | 2: Read / Write | - | 72 | Unit 4 - 106 | 6 | -
73 | True | Louver / Vane Position (0-Swing, 1-Pos1, 2-Pos2, 3-Pos3, 4-Pos4) | 16 | 0: Unsigned | 67 | - | 2: Read / Write | - | 73 | Unit 4 - 106 | 6 | -
74 | True | Room Temperature (16..30ºC) (x10) | 16 | 0: Unsigned | 68 | - | 0: Read | - | 74 | Unit 4 - 106 | 6 | -
75 | True | Filter Sign Status (0-Off, 1-On) | 16 | 0: Unsigned | 69 | - | 0: Read | - | 75 | Unit 4 - 106 | 6 | -
76 | True | Unit Error code (0-No Error,X-Error(1..255)) | 16 | 0: Unsigned | 70 | - | 0: Read | - | 76 | Unit 4 - 106 | 6 | -
77 | True | Compressor Status (0-Off, 1-On) | 16 | 0: Unsigned | 71 | - | 0: Read | - | 77 | Unit 4 - 106 | 6 | -
78 | True | Filter Sign Reset (1-Reset) | 16 | 0: Unsigned | 72 | - | 1: Trigger | - | 78 | Unit 4 - 106 | 6 | -
79 | True | RC Error Reset (1-Reset) | 16 | 0: Unsigned | 73 | - | 1: Trigger | - | 79 | Unit 4 - 106 | 6 | -
80 | True | Thermo On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 74 | - | 0: Read | - | 80 | Unit 4 - 106 | 6 | -
81 | True | Expansion valve opening pulse status (000..999) | 16 | 0: Unsigned | 75 | - | 0: Read | - | 81 | Unit 4 - 106 | 6 | -
82 | False | Decision frequency status (0..255Hz) | 16 | 0: Unsigned | 76 | - | 0: Read | - | 82 | Unit 4 - 106 | 6 | -
83 | False | Demand frequency status (0..255Hz) | 16 | 0: Unsigned | 77 | - | 0: Read | - | 83 | Unit 4 - 106 | 6 | -
84 | False | Heat Exchange low 1 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 78 | - | 0: Read | - | 84 | Unit 4 - 106 | 6 | -
85 | False | Heat Exchange low 2 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 79 | - | 0: Read | - | 85 | Unit 4 - 106 | 6 | -
86 | False | Heat Exchange low 3 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 80 | - | 0: Read | - | 86 | Unit 4 - 106 | 6 | -
87 | True | Communication Status (0-No Error, 1-Error) | 16 | 0: Unsigned | 81 | - | 0: Read | - | 87 | Unit 5 - 108 | 8 | -
88 | True | On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 82 | - | 2: Read / Write | - | 88 | Unit 5 - 108 | 8 | -
89 | True | Operation Mode (0-Cool, 1-Heat, 2-Fan, 3-Auto, 4-Dry) | 16 | 0: Unsigned | 83 | - | 2: Read / Write | - | 89 | Unit 5 - 108 | 8 | -
90 | True | Temperature Setpoint (16..30ºC) (x10) | 16 | 1: Signed (C2) | 84 | - | 2: Read / Write | - | 90 | Unit 5 - 108 | 8 | -
91 | True | Fan Speed (0-Low, 1-Medium, 2-High, 3-Powerful) | 16 | 0: Unsigned | 85 | - | 2: Read / Write | - | 91 | Unit 5 - 108 | 8 | -
92 | True | Remote Lock (0-Unlock, 1-Lock) | 16 | 0: Unsigned | 86 | - | 2: Read / Write | - | 92 | Unit 5 - 108 | 8 | -
93 | True | Louver / Vane Position (0-Swing, 1-Pos1, 2-Pos2, 3-Pos3, 4-Pos4) | 16 | 0: Unsigned | 87 | - | 2: Read / Write | - | 93 | Unit 5 - 108 | 8 | -
94 | True | Room Temperature (16..30ºC) (x10) | 16 | 0: Unsigned | 88 | - | 0: Read | - | 94 | Unit 5 - 108 | 8 | -
95 | True | Filter Sign Status (0-Off, 1-On) | 16 | 0: Unsigned | 89 | - | 0: Read | - | 95 | Unit 5 - 108 | 8 | -
96 | True | Unit Error code (0-No Error,X-Error(1..255)) | 16 | 0: Unsigned | 90 | - | 0: Read | - | 96 | Unit 5 - 108 | 8 | -
97 | True | Compressor Status (0-Off, 1-On) | 16 | 0: Unsigned | 91 | - | 0: Read | - | 97 | Unit 5 - 108 | 8 | -
98 | True | Filter Sign Reset (1-Reset) | 16 | 0: Unsigned | 92 | - | 1: Trigger | - | 98 | Unit 5 - 108 | 8 | -
99 | True | RC Error Reset (1-Reset) | 16 | 0: Unsigned | 93 | - | 1: Trigger | - | 99 | Unit 5 - 108 | 8 | -
100 | True | Thermo On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 94 | - | 0: Read | - | 100 | Unit 5 - 108 | 8 | -
101 | True | Expansion valve opening pulse status (000..999) | 16 | 0: Unsigned | 95 | - | 0: Read | - | 101 | Unit 5 - 108 | 8 | -
102 | False | Decision frequency status (0..255Hz) | 16 | 0: Unsigned | 96 | - | 0: Read | - | 102 | Unit 5 - 108 | 8 | -
103 | False | Demand frequency status (0..255Hz) | 16 | 0: Unsigned | 97 | - | 0: Read | - | 103 | Unit 5 - 108 | 8 | -
104 | False | Heat Exchange low 1 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 98 | - | 0: Read | - | 104 | Unit 5 - 108 | 8 | -
105 | False | Heat Exchange low 2 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 99 | - | 0: Read | - | 105 | Unit 5 - 108 | 8 | -
106 | False | Heat Exchange low 3 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 100 | - | 0: Read | - | 106 | Unit 5 - 108 | 8 | -
107 | True | Communication Status (0-No Error, 1-Error) | 16 | 0: Unsigned | 101 | - | 0: Read | - | 107 | Unit 6 - 110 | 10 | -
108 | True | On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 102 | - | 2: Read / Write | - | 108 | Unit 6 - 110 | 10 | -
109 | True | Operation Mode (0-Cool, 1-Heat, 2-Fan, 3-Auto, 4-Dry) | 16 | 0: Unsigned | 103 | - | 2: Read / Write | - | 109 | Unit 6 - 110 | 10 | -
110 | True | Temperature Setpoint (16..30ºC) (x10) | 16 | 1: Signed (C2) | 104 | - | 2: Read / Write | - | 110 | Unit 6 - 110 | 10 | -
111 | True | Fan Speed (0-Low, 1-Medium, 2-High, 3-Powerful) | 16 | 0: Unsigned | 105 | - | 2: Read / Write | - | 111 | Unit 6 - 110 | 10 | -
112 | True | Remote Lock (0-Unlock, 1-Lock) | 16 | 0: Unsigned | 106 | - | 2: Read / Write | - | 112 | Unit 6 - 110 | 10 | -
113 | True | Louver / Vane Position (0-Swing, 1-Pos1, 2-Pos2, 3-Pos3, 4-Pos4) | 16 | 0: Unsigned | 107 | - | 2: Read / Write | - | 113 | Unit 6 - 110 | 10 | -
114 | True | Room Temperature (16..30ºC) (x10) | 16 | 0: Unsigned | 108 | - | 0: Read | - | 114 | Unit 6 - 110 | 10 | -
115 | True | Filter Sign Status (0-Off, 1-On) | 16 | 0: Unsigned | 109 | - | 0: Read | - | 115 | Unit 6 - 110 | 10 | -
116 | True | Unit Error code (0-No Error,X-Error(1..255)) | 16 | 0: Unsigned | 110 | - | 0: Read | - | 116 | Unit 6 - 110 | 10 | -
117 | True | Compressor Status (0-Off, 1-On) | 16 | 0: Unsigned | 111 | - | 0: Read | - | 117 | Unit 6 - 110 | 10 | -
118 | True | Filter Sign Reset (1-Reset) | 16 | 0: Unsigned | 112 | - | 1: Trigger | - | 118 | Unit 6 - 110 | 10 | -
119 | True | RC Error Reset (1-Reset) | 16 | 0: Unsigned | 113 | - | 1: Trigger | - | 119 | Unit 6 - 110 | 10 | -
120 | True | Thermo On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 114 | - | 0: Read | - | 120 | Unit 6 - 110 | 10 | -
121 | True | Expansion valve opening pulse status (000..999) | 16 | 0: Unsigned | 115 | - | 0: Read | - | 121 | Unit 6 - 110 | 10 | -
122 | False | Decision frequency status (0..255Hz) | 16 | 0: Unsigned | 116 | - | 0: Read | - | 122 | Unit 6 - 110 | 10 | -
123 | False | Demand frequency status (0..255Hz) | 16 | 0: Unsigned | 117 | - | 0: Read | - | 123 | Unit 6 - 110 | 10 | -
124 | False | Heat Exchange low 1 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 118 | - | 0: Read | - | 124 | Unit 6 - 110 | 10 | -
125 | False | Heat Exchange low 2 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 119 | - | 0: Read | - | 125 | Unit 6 - 110 | 10 | -
126 | False | Heat Exchange low 3 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 120 | - | 0: Read | - | 126 | Unit 6 - 110 | 10 | -
127 | True | Communication Status (0-No Error, 1-Error) | 16 | 0: Unsigned | 121 | - | 0: Read | - | 127 | Unit 7 - 112 | 12 | -
128 | True | On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 122 | - | 2: Read / Write | - | 128 | Unit 7 - 112 | 12 | -
129 | True | Operation Mode (0-Cool, 1-Heat, 2-Fan, 3-Auto, 4-Dry) | 16 | 0: Unsigned | 123 | - | 2: Read / Write | - | 129 | Unit 7 - 112 | 12 | -
130 | True | Temperature Setpoint (16..30ºC) (x10) | 16 | 1: Signed (C2) | 124 | - | 2: Read / Write | - | 130 | Unit 7 - 112 | 12 | -
131 | True | Fan Speed (0-Low, 1-Medium, 2-High, 3-Powerful) | 16 | 0: Unsigned | 125 | - | 2: Read / Write | - | 131 | Unit 7 - 112 | 12 | -
132 | True | Remote Lock (0-Unlock, 1-Lock) | 16 | 0: Unsigned | 126 | - | 2: Read / Write | - | 132 | Unit 7 - 112 | 12 | -
133 | True | Louver / Vane Position (0-Swing, 1-Pos1, 2-Pos2, 3-Pos3, 4-Pos4) | 16 | 0: Unsigned | 127 | - | 2: Read / Write | - | 133 | Unit 7 - 112 | 12 | -
134 | True | Room Temperature (16..30ºC) (x10) | 16 | 0: Unsigned | 128 | - | 0: Read | - | 134 | Unit 7 - 112 | 12 | -
135 | True | Filter Sign Status (0-Off, 1-On) | 16 | 0: Unsigned | 129 | - | 0: Read | - | 135 | Unit 7 - 112 | 12 | -
136 | True | Unit Error code (0-No Error,X-Error(1..255)) | 16 | 0: Unsigned | 130 | - | 0: Read | - | 136 | Unit 7 - 112 | 12 | -
137 | True | Compressor Status (0-Off, 1-On) | 16 | 0: Unsigned | 131 | - | 0: Read | - | 137 | Unit 7 - 112 | 12 | -
138 | True | Filter Sign Reset (1-Reset) | 16 | 0: Unsigned | 132 | - | 1: Trigger | - | 138 | Unit 7 - 112 | 12 | -
139 | True | RC Error Reset (1-Reset) | 16 | 0: Unsigned | 133 | - | 1: Trigger | - | 139 | Unit 7 - 112 | 12 | -
140 | True | Thermo On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 134 | - | 0: Read | - | 140 | Unit 7 - 112 | 12 | -
141 | True | Expansion valve opening pulse status (000..999) | 16 | 0: Unsigned | 135 | - | 0: Read | - | 141 | Unit 7 - 112 | 12 | -
142 | False | Decision frequency status (0..255Hz) | 16 | 0: Unsigned | 136 | - | 0: Read | - | 142 | Unit 7 - 112 | 12 | -
143 | False | Demand frequency status (0..255Hz) | 16 | 0: Unsigned | 137 | - | 0: Read | - | 143 | Unit 7 - 112 | 12 | -
144 | False | Heat Exchange low 1 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 138 | - | 0: Read | - | 144 | Unit 7 - 112 | 12 | -
145 | False | Heat Exchange low 2 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 139 | - | 0: Read | - | 145 | Unit 7 - 112 | 12 | -
146 | False | Heat Exchange low 3 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 140 | - | 0: Read | - | 146 | Unit 7 - 112 | 12 | -
147 | True | Communication Status (0-No Error, 1-Error) | 16 | 0: Unsigned | 141 | - | 0: Read | - | 147 | Unit 8 - 201 | 21 | -
148 | True | On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 142 | - | 2: Read / Write | - | 148 | Unit 8 - 201 | 21 | -
149 | True | Operation Mode (0-Cool, 1-Heat, 2-Fan, 3-Auto, 4-Dry) | 16 | 0: Unsigned | 143 | - | 2: Read / Write | - | 149 | Unit 8 - 201 | 21 | -
150 | True | Temperature Setpoint (16..30ºC) (x10) | 16 | 1: Signed (C2) | 144 | - | 2: Read / Write | - | 150 | Unit 8 - 201 | 21 | -
151 | True | Fan Speed (0-Low, 1-Medium, 2-High, 3-Powerful) | 16 | 0: Unsigned | 145 | - | 2: Read / Write | - | 151 | Unit 8 - 201 | 21 | -
152 | True | Remote Lock (0-Unlock, 1-Lock) | 16 | 0: Unsigned | 146 | - | 2: Read / Write | - | 152 | Unit 8 - 201 | 21 | -
153 | True | Louver / Vane Position (0-Swing, 1-Pos1, 2-Pos2, 3-Pos3, 4-Pos4) | 16 | 0: Unsigned | 147 | - | 2: Read / Write | - | 153 | Unit 8 - 201 | 21 | -
154 | True | Room Temperature (16..30ºC) (x10) | 16 | 0: Unsigned | 148 | - | 0: Read | - | 154 | Unit 8 - 201 | 21 | -
155 | True | Filter Sign Status (0-Off, 1-On) | 16 | 0: Unsigned | 149 | - | 0: Read | - | 155 | Unit 8 - 201 | 21 | -
156 | True | Unit Error code (0-No Error,X-Error(1..255)) | 16 | 0: Unsigned | 150 | - | 0: Read | - | 156 | Unit 8 - 201 | 21 | -
157 | True | Compressor Status (0-Off, 1-On) | 16 | 0: Unsigned | 151 | - | 0: Read | - | 157 | Unit 8 - 201 | 21 | -
158 | True | Filter Sign Reset (1-Reset) | 16 | 0: Unsigned | 152 | - | 1: Trigger | - | 158 | Unit 8 - 201 | 21 | -
159 | True | RC Error Reset (1-Reset) | 16 | 0: Unsigned | 153 | - | 1: Trigger | - | 159 | Unit 8 - 201 | 21 | -
160 | True | Thermo On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 154 | - | 0: Read | - | 160 | Unit 8 - 201 | 21 | -
161 | True | Expansion valve opening pulse status (000..999) | 16 | 0: Unsigned | 155 | - | 0: Read | - | 161 | Unit 8 - 201 | 21 | -
162 | False | Decision frequency status (0..255Hz) | 16 | 0: Unsigned | 156 | - | 0: Read | - | 162 | Unit 8 - 201 | 21 | -
163 | False | Demand frequency status (0..255Hz) | 16 | 0: Unsigned | 157 | - | 0: Read | - | 163 | Unit 8 - 201 | 21 | -
164 | False | Heat Exchange low 1 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 158 | - | 0: Read | - | 164 | Unit 8 - 201 | 21 | -
165 | False | Heat Exchange low 2 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 159 | - | 0: Read | - | 165 | Unit 8 - 201 | 21 | -
166 | False | Heat Exchange low 3 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 160 | - | 0: Read | - | 166 | Unit 8 - 201 | 21 | -
167 | True | Communication Status (0-No Error, 1-Error) | 16 | 0: Unsigned | 161 | - | 0: Read | - | 167 | Unit 9 - 202 | 22 | -
168 | True | On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 162 | - | 2: Read / Write | - | 168 | Unit 9 - 202 | 22 | -
169 | True | Operation Mode (0-Cool, 1-Heat, 2-Fan, 3-Auto, 4-Dry) | 16 | 0: Unsigned | 163 | - | 2: Read / Write | - | 169 | Unit 9 - 202 | 22 | -
170 | True | Temperature Setpoint (16..30ºC) (x10) | 16 | 1: Signed (C2) | 164 | - | 2: Read / Write | - | 170 | Unit 9 - 202 | 22 | -
171 | True | Fan Speed (0-Low, 1-Medium, 2-High, 3-Powerful) | 16 | 0: Unsigned | 165 | - | 2: Read / Write | - | 171 | Unit 9 - 202 | 22 | -
172 | True | Remote Lock (0-Unlock, 1-Lock) | 16 | 0: Unsigned | 166 | - | 2: Read / Write | - | 172 | Unit 9 - 202 | 22 | -
173 | True | Louver / Vane Position (0-Swing, 1-Pos1, 2-Pos2, 3-Pos3, 4-Pos4) | 16 | 0: Unsigned | 167 | - | 2: Read / Write | - | 173 | Unit 9 - 202 | 22 | -
174 | True | Room Temperature (16..30ºC) (x10) | 16 | 0: Unsigned | 168 | - | 0: Read | - | 174 | Unit 9 - 202 | 22 | -
175 | True | Filter Sign Status (0-Off, 1-On) | 16 | 0: Unsigned | 169 | - | 0: Read | - | 175 | Unit 9 - 202 | 22 | -
176 | True | Unit Error code (0-No Error,X-Error(1..255)) | 16 | 0: Unsigned | 170 | - | 0: Read | - | 176 | Unit 9 - 202 | 22 | -
177 | True | Compressor Status (0-Off, 1-On) | 16 | 0: Unsigned | 171 | - | 0: Read | - | 177 | Unit 9 - 202 | 22 | -
178 | True | Filter Sign Reset (1-Reset) | 16 | 0: Unsigned | 172 | - | 1: Trigger | - | 178 | Unit 9 - 202 | 22 | -
179 | True | RC Error Reset (1-Reset) | 16 | 0: Unsigned | 173 | - | 1: Trigger | - | 179 | Unit 9 - 202 | 22 | -
180 | True | Thermo On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 174 | - | 0: Read | - | 180 | Unit 9 - 202 | 22 | -
181 | True | Expansion valve opening pulse status (000..999) | 16 | 0: Unsigned | 175 | - | 0: Read | - | 181 | Unit 9 - 202 | 22 | -
182 | False | Decision frequency status (0..255Hz) | 16 | 0: Unsigned | 176 | - | 0: Read | - | 182 | Unit 9 - 202 | 22 | -
183 | False | Demand frequency status (0..255Hz) | 16 | 0: Unsigned | 177 | - | 0: Read | - | 183 | Unit 9 - 202 | 22 | -
184 | False | Heat Exchange low 1 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 178 | - | 0: Read | - | 184 | Unit 9 - 202 | 22 | -
185 | False | Heat Exchange low 2 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 179 | - | 0: Read | - | 185 | Unit 9 - 202 | 22 | -
186 | False | Heat Exchange low 3 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 180 | - | 0: Read | - | 186 | Unit 9 - 202 | 22 | -
187 | True | Communication Status (0-No Error, 1-Error) | 16 | 0: Unsigned | 181 | - | 0: Read | - | 187 | Unit 10 - 203 | 23 | -
188 | True | On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 182 | - | 2: Read / Write | - | 188 | Unit 10 - 203 | 23 | -
189 | True | Operation Mode (0-Cool, 1-Heat, 2-Fan, 3-Auto, 4-Dry) | 16 | 0: Unsigned | 183 | - | 2: Read / Write | - | 189 | Unit 10 - 203 | 23 | -
190 | True | Temperature Setpoint (16..30ºC) (x10) | 16 | 1: Signed (C2) | 184 | - | 2: Read / Write | - | 190 | Unit 10 - 203 | 23 | -
191 | True | Fan Speed (0-Low, 1-Medium, 2-High, 3-Powerful) | 16 | 0: Unsigned | 185 | - | 2: Read / Write | - | 191 | Unit 10 - 203 | 23 | -
192 | True | Remote Lock (0-Unlock, 1-Lock) | 16 | 0: Unsigned | 186 | - | 2: Read / Write | - | 192 | Unit 10 - 203 | 23 | -
193 | True | Louver / Vane Position (0-Swing, 1-Pos1, 2-Pos2, 3-Pos3, 4-Pos4) | 16 | 0: Unsigned | 187 | - | 2: Read / Write | - | 193 | Unit 10 - 203 | 23 | -
194 | True | Room Temperature (16..30ºC) (x10) | 16 | 0: Unsigned | 188 | - | 0: Read | - | 194 | Unit 10 - 203 | 23 | -
195 | True | Filter Sign Status (0-Off, 1-On) | 16 | 0: Unsigned | 189 | - | 0: Read | - | 195 | Unit 10 - 203 | 23 | -
196 | True | Unit Error code (0-No Error,X-Error(1..255)) | 16 | 0: Unsigned | 190 | - | 0: Read | - | 196 | Unit 10 - 203 | 23 | -
197 | True | Compressor Status (0-Off, 1-On) | 16 | 0: Unsigned | 191 | - | 0: Read | - | 197 | Unit 10 - 203 | 23 | -
198 | True | Filter Sign Reset (1-Reset) | 16 | 0: Unsigned | 192 | - | 1: Trigger | - | 198 | Unit 10 - 203 | 23 | -
199 | True | RC Error Reset (1-Reset) | 16 | 0: Unsigned | 193 | - | 1: Trigger | - | 199 | Unit 10 - 203 | 23 | -
200 | True | Thermo On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 194 | - | 0: Read | - | 200 | Unit 10 - 203 | 23 | -
201 | True | Expansion valve opening pulse status (000..999) | 16 | 0: Unsigned | 195 | - | 0: Read | - | 201 | Unit 10 - 203 | 23 | -
202 | False | Decision frequency status (0..255Hz) | 16 | 0: Unsigned | 196 | - | 0: Read | - | 202 | Unit 10 - 203 | 23 | -
203 | False | Demand frequency status (0..255Hz) | 16 | 0: Unsigned | 197 | - | 0: Read | - | 203 | Unit 10 - 203 | 23 | -
204 | False | Heat Exchange low 1 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 198 | - | 0: Read | - | 204 | Unit 10 - 203 | 23 | -
205 | False | Heat Exchange low 2 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 199 | - | 0: Read | - | 205 | Unit 10 - 203 | 23 | -
206 | False | Heat Exchange low 3 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 200 | - | 0: Read | - | 206 | Unit 10 - 203 | 23 | -
207 | True | Communication Status (0-No Error, 1-Error) | 16 | 0: Unsigned | 201 | - | 0: Read | - | 207 | Unit 11 - 205 | 25 | -
208 | True | On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 202 | - | 2: Read / Write | - | 208 | Unit 11 - 205 | 25 | -
209 | True | Operation Mode (0-Cool, 1-Heat, 2-Fan, 3-Auto, 4-Dry) | 16 | 0: Unsigned | 203 | - | 2: Read / Write | - | 209 | Unit 11 - 205 | 25 | -
210 | True | Temperature Setpoint (16..30ºC) (x10) | 16 | 1: Signed (C2) | 204 | - | 2: Read / Write | - | 210 | Unit 11 - 205 | 25 | -
211 | True | Fan Speed (0-Low, 1-Medium, 2-High, 3-Powerful) | 16 | 0: Unsigned | 205 | - | 2: Read / Write | - | 211 | Unit 11 - 205 | 25 | -
212 | True | Remote Lock (0-Unlock, 1-Lock) | 16 | 0: Unsigned | 206 | - | 2: Read / Write | - | 212 | Unit 11 - 205 | 25 | -
213 | True | Louver / Vane Position (0-Swing, 1-Pos1, 2-Pos2, 3-Pos3, 4-Pos4) | 16 | 0: Unsigned | 207 | - | 2: Read / Write | - | 213 | Unit 11 - 205 | 25 | -
214 | True | Room Temperature (16..30ºC) (x10) | 16 | 0: Unsigned | 208 | - | 0: Read | - | 214 | Unit 11 - 205 | 25 | -
215 | True | Filter Sign Status (0-Off, 1-On) | 16 | 0: Unsigned | 209 | - | 0: Read | - | 215 | Unit 11 - 205 | 25 | -
216 | True | Unit Error code (0-No Error,X-Error(1..255)) | 16 | 0: Unsigned | 210 | - | 0: Read | - | 216 | Unit 11 - 205 | 25 | -
217 | True | Compressor Status (0-Off, 1-On) | 16 | 0: Unsigned | 211 | - | 0: Read | - | 217 | Unit 11 - 205 | 25 | -
218 | True | Filter Sign Reset (1-Reset) | 16 | 0: Unsigned | 212 | - | 1: Trigger | - | 218 | Unit 11 - 205 | 25 | -
219 | True | RC Error Reset (1-Reset) | 16 | 0: Unsigned | 213 | - | 1: Trigger | - | 219 | Unit 11 - 205 | 25 | -
220 | True | Thermo On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 214 | - | 0: Read | - | 220 | Unit 11 - 205 | 25 | -
221 | True | Expansion valve opening pulse status (000..999) | 16 | 0: Unsigned | 215 | - | 0: Read | - | 221 | Unit 11 - 205 | 25 | -
222 | False | Decision frequency status (0..255Hz) | 16 | 0: Unsigned | 216 | - | 0: Read | - | 222 | Unit 11 - 205 | 25 | -
223 | False | Demand frequency status (0..255Hz) | 16 | 0: Unsigned | 217 | - | 0: Read | - | 223 | Unit 11 - 205 | 25 | -
224 | False | Heat Exchange low 1 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 218 | - | 0: Read | - | 224 | Unit 11 - 205 | 25 | -
225 | False | Heat Exchange low 2 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 219 | - | 0: Read | - | 225 | Unit 11 - 205 | 25 | -
226 | False | Heat Exchange low 3 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 220 | - | 0: Read | - | 226 | Unit 11 - 205 | 25 | -