## Signals
Intesis MAPS Excel signals file
PROJECT_NAME | Project1
Intesis MAPS Version | 1.2.31.0
Internal Protocol | Modbus Slave
External Protocol | Mitsubishi Heavy Industries
Timestamp | 07/27/2026
# | Active | Description | Data Length | Format | Address | Bit | Read / Write | String Length | # | Unit ID | IU | OU
1 | True | Gateway Communication Status (0-No Error, 1-Failure) | 16 | 0: Unsigned | 2995 | - | 0: Read | - | 1 | - | - | -
2 | True | On/Off (all the units) (0-Off, 1-On) | 16 | 0: Unsigned | 2996 | - | 2: Read / Write | - | 2 | - | - | -
3 | True | Operation Mode (all the units) (0-Cool, 1-Heat, 2-Fan, 3-Auto, 4-Dry) | 16 | 0: Unsigned | 2997 | - | 2: Read / Write | - | 3 | - | - | -
4 | True | Setpoint (all the units) (16..30ºC) (x10) | 16 | 1: Signed (C2) | 2998 | - | 2: Read / Write | - | 4 | - | - | -
5 | True | Fan Speed (all the units) (0-Low, 1-Medium, 2-High, 3-Powerful) | 16 | 0: Unsigned | 2999 | - | 2: Read / Write | - | 5 | - | - | -
6 | True | Remote Lock (all the units) (1-Lock, 0-Unlock) | 16 | 0: Unsigned | 3000 | - | 2: Read / Write | - | 6 | - | - | -
7 | True | Communication Status (0-No Error, 1-Error) | 16 | 0: Unsigned | 1 | - | 0: Read | - | 7 | Unit 1 - Indoor Unit 1 | 0 | -
8 | True | On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 2 | - | 2: Read / Write | - | 8 | Unit 1 - Indoor Unit 1 | 0 | -
9 | True | Operation Mode (0-Cool, 1-Heat, 2-Fan, 3-Auto, 4-Dry) | 16 | 0: Unsigned | 3 | - | 2: Read / Write | - | 9 | Unit 1 - Indoor Unit 1 | 0 | -
10 | True | Temperature Setpoint (16..30ºC) (x10) | 16 | 1: Signed (C2) | 4 | - | 2: Read / Write | - | 10 | Unit 1 - Indoor Unit 1 | 0 | -
11 | True | Fan Speed (0-Low, 1-Medium, 2-High, 3-Powerful) | 16 | 0: Unsigned | 5 | - | 2: Read / Write | - | 11 | Unit 1 - Indoor Unit 1 | 0 | -
12 | True | Remote Lock (0-Unlock, 1-Lock) | 16 | 0: Unsigned | 6 | - | 2: Read / Write | - | 12 | Unit 1 - Indoor Unit 1 | 0 | -
13 | True | Louver / Vane Position (0-Swing, 1-Pos1, 2-Pos2, 3-Pos3, 4-Pos4) | 16 | 0: Unsigned | 7 | - | 2: Read / Write | - | 13 | Unit 1 - Indoor Unit 1 | 0 | -
14 | True | Room Temperature (16..30ºC) (x10) | 16 | 0: Unsigned | 8 | - | 0: Read | - | 14 | Unit 1 - Indoor Unit 1 | 0 | -
15 | True | Filter Sign Status (0-Off, 1-On) | 16 | 0: Unsigned | 9 | - | 0: Read | - | 15 | Unit 1 - Indoor Unit 1 | 0 | -
16 | True | Unit Error code (0-No Error,X-Error(1..255)) | 16 | 0: Unsigned | 10 | - | 0: Read | - | 16 | Unit 1 - Indoor Unit 1 | 0 | -
17 | True | Compressor Status (0-Off, 1-On) | 16 | 0: Unsigned | 11 | - | 0: Read | - | 17 | Unit 1 - Indoor Unit 1 | 0 | -
18 | True | Filter Sign Reset (1-Reset) | 16 | 0: Unsigned | 12 | - | 1: Trigger | - | 18 | Unit 1 - Indoor Unit 1 | 0 | -
19 | True | RC Error Reset (1-Reset) | 16 | 0: Unsigned | 13 | - | 1: Trigger | - | 19 | Unit 1 - Indoor Unit 1 | 0 | -
20 | True | Thermo On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 14 | - | 0: Read | - | 20 | Unit 1 - Indoor Unit 1 | 0 | -
21 | True | Expansion valve opening pulse status (000..999) | 16 | 0: Unsigned | 15 | - | 0: Read | - | 21 | Unit 1 - Indoor Unit 1 | 0 | -
22 | False | Decision frequency status (0..255Hz) | 16 | 0: Unsigned | 16 | - | 0: Read | - | 22 | Unit 1 - Indoor Unit 1 | 0 | -
23 | False | Demand frequency status (0..255Hz) | 16 | 0: Unsigned | 17 | - | 0: Read | - | 23 | Unit 1 - Indoor Unit 1 | 0 | -
24 | False | Heat Exchange low 1 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 18 | - | 0: Read | - | 24 | Unit 1 - Indoor Unit 1 | 0 | -
25 | False | Heat Exchange low 2 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 19 | - | 0: Read | - | 25 | Unit 1 - Indoor Unit 1 | 0 | -
26 | False | Heat Exchange low 3 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 20 | - | 0: Read | - | 26 | Unit 1 - Indoor Unit 1 | 0 | -
27 | True | Communication Status (0-No Error, 1-Error) | 16 | 0: Unsigned | 21 | - | 0: Read | - | 27 | Unit 2 - Indoor Unit 2 | 25 | -
28 | True | On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 22 | - | 2: Read / Write | - | 28 | Unit 2 - Indoor Unit 2 | 25 | -
29 | True | Operation Mode (0-Cool, 1-Heat, 2-Fan, 3-Auto, 4-Dry) | 16 | 0: Unsigned | 23 | - | 2: Read / Write | - | 29 | Unit 2 - Indoor Unit 2 | 25 | -
30 | True | Temperature Setpoint (16..30ºC) (x10) | 16 | 1: Signed (C2) | 24 | - | 2: Read / Write | - | 30 | Unit 2 - Indoor Unit 2 | 25 | -
31 | True | Fan Speed (0-Low, 1-Medium, 2-High, 3-Powerful) | 16 | 0: Unsigned | 25 | - | 2: Read / Write | - | 31 | Unit 2 - Indoor Unit 2 | 25 | -
32 | True | Remote Lock (0-Unlock, 1-Lock) | 16 | 0: Unsigned | 26 | - | 2: Read / Write | - | 32 | Unit 2 - Indoor Unit 2 | 25 | -
33 | True | Louver / Vane Position (0-Swing, 1-Pos1, 2-Pos2, 3-Pos3, 4-Pos4) | 16 | 0: Unsigned | 27 | - | 2: Read / Write | - | 33 | Unit 2 - Indoor Unit 2 | 25 | -
34 | True | Room Temperature (16..30ºC) (x10) | 16 | 0: Unsigned | 28 | - | 0: Read | - | 34 | Unit 2 - Indoor Unit 2 | 25 | -
35 | True | Filter Sign Status (0-Off, 1-On) | 16 | 0: Unsigned | 29 | - | 0: Read | - | 35 | Unit 2 - Indoor Unit 2 | 25 | -
36 | True | Unit Error code (0-No Error,X-Error(1..255)) | 16 | 0: Unsigned | 30 | - | 0: Read | - | 36 | Unit 2 - Indoor Unit 2 | 25 | -
37 | True | Compressor Status (0-Off, 1-On) | 16 | 0: Unsigned | 31 | - | 0: Read | - | 37 | Unit 2 - Indoor Unit 2 | 25 | -
38 | True | Filter Sign Reset (1-Reset) | 16 | 0: Unsigned | 32 | - | 1: Trigger | - | 38 | Unit 2 - Indoor Unit 2 | 25 | -
39 | True | RC Error Reset (1-Reset) | 16 | 0: Unsigned | 33 | - | 1: Trigger | - | 39 | Unit 2 - Indoor Unit 2 | 25 | -
40 | True | Thermo On/Off (0-Off, 1-On) | 16 | 0: Unsigned | 34 | - | 0: Read | - | 40 | Unit 2 - Indoor Unit 2 | 25 | -
41 | True | Expansion valve opening pulse status (000..999) | 16 | 0: Unsigned | 35 | - | 0: Read | - | 41 | Unit 2 - Indoor Unit 2 | 25 | -
42 | False | Decision frequency status (0..255Hz) | 16 | 0: Unsigned | 36 | - | 0: Read | - | 42 | Unit 2 - Indoor Unit 2 | 25 | -
43 | False | Demand frequency status (0..255Hz) | 16 | 0: Unsigned | 37 | - | 0: Read | - | 43 | Unit 2 - Indoor Unit 2 | 25 | -
44 | False | Heat Exchange low 1 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 38 | - | 0: Read | - | 44 | Unit 2 - Indoor Unit 2 | 25 | -
45 | False | Heat Exchange low 2 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 39 | - | 0: Read | - | 45 | Unit 2 - Indoor Unit 2 | 25 | -
46 | False | Heat Exchange low 3 temperature (ºC) (x10) | 16 | 1: Signed (C2) | 40 | - | 0: Read | - | 46 | Unit 2 - Indoor Unit 2 | 25 | -